## Slide 1
Risk Management
State Electrical Division
North Carolina Department of Insurance
Office of State Fire Marshal
2017 State Electrical Code
90.2(B)(5) Utility Conductors
and Equipment

## Slide 2
Notice:
The following illustrations are approved by the State Electrical Division of the North Carolina Department of Insurance, Office of State Fire Marshal. These illustrations are intended to demonstrate but not supersede the official written interpretations found at the following web address:
http://www.ncdoi.com/OSFM/State_Electrical_Division//Default.aspx?field1=State_Electrical_Code_and_Interpretations
Joseph Starling
Chief State Electrical Engineer & Inspector
Illustrated by:
Danny Thomas
State Electrical Inspector

## Slide 3
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Question 1:
If service drop or lateral conductors are installed under the control of the electrical utility, does the State Electrical Code have jurisdiction to regulate any portion of the utility’s installation?
ON
OFF
Utility Transformer
Utility Transformer
400 amp

## Slide 4
Answer 1:
The State Electrical Code includes the 2017 NEC with State amendments. Section 90.2(B)(5) of the NEC designates electrical utility service drop or lateral installations as “Not Covered” within the scope of the NEC; thus such utility drop or lateral conductors cannot be governed by the State Electrical Code. Additionally, there is no exception that grants the State Electrical Code the authority to regulate electrical utility service drop or lateral installations when installed within customer owned equipment.
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019

## Slide 5
Answer 2:
Illustration
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
(B) Not Covered. This Code does not cover the following:
(5) Installations under the exclusive control of an electric
utility where such installations a. Consist of service drops or service laterals, and associated
metering,
90.2 Scope.
Covered. This Code covers the installation and removal of electrical conductors, equipment, and raceways; signaling and communications conductors, equipment, and raceways; and optical fiber cables and raceways for the following:
Public and private premises,
including buildings, structures,

## Slide 6
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Question 2:
If the electrical utility’s service drop or lateral conductors are installed under the terminal lugs of a customer owned molded case breaker (which is the service disconnect), must extra provisions be made to insure the electrical utility conductors do not violate sections 240.4(B), 240.4(C) or 310.15 of the State Electrical Code?
ON
OFF
Utility Transformer
Utility Transformer
400 amp
Building Service Equipment (Customer Owned)

## Slide 7
Answer 2:
Sections 240.4(B) and 240.4(C) are restrictions for the ampacity of overcurrent devices with respect to the conductors being protected by such devices. Sections 310.15 generally regulates the ampacity of electrical conductors. The State Electrical Division interprets sections of 240.4(B), 240.4(C), and 310.15 as being applicable only to within the NEC’s scope.
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
The State Electrical Division interprets the “service point” in Article 100 as the specific location in the electrical system that separates the State Electrical Code’s jurisdiction from the electrical utility's jurisdiction. The State Electrical Code stays silent on the method of connection required to create the “service point”. If the lugs on a molded circuit breaker installed by the Electrical Contractor is the method of connection to the electrical utility, then the State Electrical Code’s jurisdiction ceases where the lug makes contact with the utility conductor. Therefore, the Electrical Inspector’s jurisdiction to enforce the State Electrical code also ceases where the lug makes contact with the uitity contractor.

## Slide 8
Answer 2:
Illustration
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Service Point as defined in Article 100 of the NEC.
ON
OFF
Utility Transformer
Utility Transformer
400 amp
Customer owned service equipment with molded case circuit breaker as the service disconnect.
Utility's service lateral conductors
Wiring does not fall under NEC requirements until the load side of the molded case circuit breaker.

## Slide 9
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Question 3:
Can a “certificate of compliance” be withheld or denied for an electrical installation that is regulated by the State Electrical Code and does not comply with provisions required by the serving electrical utility?
Certificate of Compliance
Installation does meet the State Electrical Code Requirements
Installation does not meet the State Electrical Code Requirements
Inspector Date

## Slide 10
Answer 3:
Electrical installations that meet the provisions of the State Electrical Code are entitled to a certificate of compliance in accordance with section 204.8.2 of the NC Administrative Code and Policies. Compliance with the “Duke Energy White Book”, adherence to site plans when the installation is Code prescriptive, or installations that exceed the scope of the NEC as described in section 90.2(B).
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019

## Slide 11
Answer 3:
Illustration
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Certificate of Compliance
This installation does meet the State Electrical Code Requirements
This installation does not meet the State Electrical Code Requirements
Inspector Date
John Doe 1/22/2019

## Slide 12
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Question 4:
Who determines where the “service point” will be located?
ON
OFF
Utility Transformer
Utility Transformer
400 amp

## Slide 13
Answer 4:
The service point can be described as the point of demarcation between where the serving utility ends and the premises wiring begins. The serving utility generally specifies the location of the service point based on the “conditions of service.” 2017 NEC Article 100 Definition of Service Point Informational Note.
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019

## Slide 14
Answer 4:
Illustration 1
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
“point of demarcation between where the serving utility ends and the premises wiring begins”
Utility's service lateral conductors
Service Point as defined in Article 100 of the NEC.

## Slide 15
Answer 4:
Illustration 2
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Service Point
“point of demarcation between where the serving utility ends and the premises wiring begins”

## Slide 16
Answer 4:
Illustration 3
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Utility Transformer
Utility Transformer
Service Point as defined in Article 100 of the NEC.
“point of demarcation between where the serving utility ends and the premises wiring begins”
(If utility service lateral conductors.)

## Slide 17
Answer 4:
Illustration 4
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Utility Transformer
Utility Transformer
Service Point as defined in Article 100 of the NEC.
“point of demarcation between where the serving utility ends and the premises wiring begins”
(Only if customer owned conductors.)

## Slide 18
Answer 4:
Illustration 5
2017 Electrical Code
Section: 90.2(B)(5)
Subject: Electrical Utility Conductors
Date: February 19, 2019
Service Point
“point of demarcation between where the serving utility ends and the premises wiring begins”