## Input
2018 NCEBC Chapter 14 Evaluation
General Building Information |  | 1401.6.7: HVAC Systems |  |  |  | 1401.6.17: Automatic Sprinklers
Occupancy | R1 | HVAC System Category |  |  | Category b | Sprinkler System Category |  |  | Category c
Construction Type | IIA | SAFETY PARAMETER (FS) (ME) (GS) |  |  | -5 | SAFETY PARAMETER (FS) (ME/2) (GS) |  |  | 0
Is the Building Fully Sprinklered? | NFPA 13
|  | 1401.6.8: Automatic Fire Detection |  |  |  | 1401.6.18: Standpipes
1401.6.1.: Building Height |  | Automatic Fire Detection Category |  |  | Category b | Standpipe System Category |  |  | Category a
Allowable Height, ft (NCBC Table 504.3) | 65 | SAFETY PARAMETER (FS) (ME) (GS) |  |  | -5 | SAFETY PARAMETER (FS) (ME) (GS) |  |  | -6
Allowable Height, ft (NCBC Table 504.3 Sprinkler) | 85
Existing Building Height, ft | 39 | 1401.6.9: Fire Alarm Systems |  |  |  | 1401.6.19: Incidental Use
Allowable Height in stories, NCBC 504.4 | 5 | Fire Alarm Category |  |  | Category b | Are there incidental use areas in the building area? |  |  | Yes
Existing Building Height in stories | 1 | SAFETY PARAMETER (FS) (ME) (GS) |  |  | -5
Construction Factor | 1 |  |  |  |  | Protection Provided |  |  | None
|  | 1401.6.10: Smoke Control |  |  |  | Protection Required (Table 509) |  |  | 1 Hour
Height Value, ft (Eq. 14-1) | 3.68 | Smoke Control Category |  |  | Category a
Height Value, stories (Eq. 14-2) | 4 | SAFETY PARAMETER (ME) (GS) |  |  | 0 | SAFETY PARAMETER (FS) (ME) (GS) |  |  | -1
SAFETY PARAMETER (FS) (ME) (GS) | 3.68
|  | 1401.6.11: Means of Egress |  |  |  | 1401.6.20 Smoke Compartmentation
1401.6.2: Building Area |  | Means of Egress Category |  |  | Category c | Smoke Compartmentation Category |  |  | Category b
Perimeter of Entire Building, ft | 3600 | SAFETY PARAMETER (ME) (GS) |  |  | 0 | SAFETY PARAMETER (FS) (ME) (GS) |  |  | 0
Perimeter that fronts on public way, ≥20 ft | 1500
Width of public way, ft W from Equation 5-4 NCBC | 30 | 1401.6.12: Dead Ends |  |  |  | 1401.6.21 I-2 Occupancy Specifications
Tabular Area per story (NCBC Table 506.2) | 24000 | Maximum Dead End Length, ft |  |  | 70 |  | 1401.6.21.1 Patient ability for self preservation
Actual Building Area, sq ft | 24000 | Dead End Width, ft |  |  | 5 |  | Self Preservation Category |  | Category a
Area Increase Factor for sprinklers | 3 | SAFETY PARAMETER (ME) (GS) |  |  | -2 |  | SAFETY PARAMETER (ME) (GS) |  | 0
Area Increase Factor for frontage | 0.17 | [5 empty] | 1401.6.21.2 Patient concentration
Allowable Area, per floor, sq ft | 100080 | 1401.6.13: Maximum Exit Access Travel Distance |  |  |  |  | Patient Concentration Category |  | Category b
|  | Maximum Actual Travel Distance, ft |  |  | 270 |  | SAFETY PARAMETER (ME) (GS) |  | 0
Area Value (Eq. 14-4) | 63.4 | Single Exit? | No | If yes, Story? |  |  | 1401.6.21.3 Attendent to patient ratio
SAFETY PARAMETER (FS) (ME) (GS) | 10.5 | Maximum Allowable Travel Distance, ft |  |  | 250 |  | Attendent to Patient Ratio Category |  | Category a
|  | SAFETY PARAMETER (ME) (GS) |  |  | -1.6 |  | SAFETY PARAMETER (ME) (GS) |  | 0
1401.6.3: Compartmentation
Compartment Size, sq ft | 10001 | 1401.6.14: Elevator Control
|  | Elevator Control Category |  |  | Category c | SUMMARY
Compartmentation Value (CV) | 0 | Less than 25 ft of travel above or below the primary level of elevator access for emergency personnel? |  |  | No | Mandatory Safety Scores
SAFETY PARAMETER (FS) (ME) (GS) | 0 |  |  |  |  | Mandatory Fire Safety |  | (MFS) | 21
[6 empty] | Mandatory Means of Egress |  | (MME) | 38
1401.6.4: Tenant & Dwelling Unit Separations | [5 empty] | Mandatory General Safety |  | (MGS) | 38
Unit Separation Category | Category c | SAFETY PARAMETER (FS) (ME) (GS) |  |  | 0
SAFETY PARAMETER (FS) (ME) (GS) | 0 |  |  |  |  | Building Score Total Values
|  | 1401.6.15: Means of Egress Emergency Lighting |  |  |  | Fire Safety |  | (FS) | -15.82 | FAIL
1401.6.5: Corridor Walls |  | Means of Egress Lighting Category |  |  | Category c | Means of Egress |  | (ME) | -5.42 | FAIL
Corridor Walls Category | Category c | Two or more exits? |  |  | Yes | General Safety |  | (GS) | -15.42 | FAIL
SAFETY PARAMETER (FS) (ME) (GS) | 0 | SAFETY PARAMETER (ME) (GS) |  |  | 4
Notes:
1401.6.6: Vertical Openings |  | 1401.6.16 Mixed Occupancies
Maximum Number of Floors Connected | 1 | Mixed Occupancy Category |  |  | Category a
Type of Protection | None | Does the building have mixed occupancies? |  |  | Yes
Protection Value | N/A
Construction Type Factor | 2.2 | Is there separation between the mixed occupancies? |  |  | Yes
Vertical Opening Value (Eq. 14-5) | N/A
SAFETY PARAMETER (FS) (ME) (GS) | 2 | SAFETY PARAMETER (FS) (GS) |  |  | -10
Note on A1: The evaluation process specified herein shall be followed in its entirety to evaluate existing buildings in Groups A, B, E, F, M, R, S and U. For existing buildings in Group I-2, the evaluation process specified herein shall be followed and applied to each and every individual smoke compartment. Table 1401.7 shall be utilized for tabulating the results of the evaluation. References to other sections of this code indicate that compliance with those sections is required in order to gain credit in the evaluation herein outlined. In applying this section to a building with mixed occupancies, where the separation between the mixed occupancies does not qualify for any category indicated in Section 1401.6.16, the score for each occupancy shall be determined, and the lower score determined for each section of the evaluation process shall apply to the entire building, or to each smoke compartment for Group I-2 occupancies. Where the separation between the mixed occupancies qualifies for any category indicated in section 1401.6.16, the score for each occupancy shall apply to portion, or smoke compartment of the building based on the occupancy of the space.
Note on D4: ◄Select the Occupancy Classification. That the existing building is changing to per Chapter 3 of the NCBC
Note on J4: ◄Category a—Plenums not in accordance with Section 602 of the International Mechanical Code. -10 points. Category b—Air movement in egress elements not in accordance with Section 1018.5 of the NC Building Code. -5 points. Category c—Both categories a and b are applicable. -15 points. Category d—Compliance of the HVAC system with Section 1020.5 of the NC Building Code and Section 602 of the International Mechanical Code. 0 points. Category e—Systems serving one story; or a central boiler/chiller system without ductwork connecting two or more stories. 5 points.
Note on P4: ◄Category a—Sprinklers are required throughout; sprinkler protection is not provided or the sprinkler system design is not adequate for the hazard protected in accordance with Section 903 of the NCBC. Category b—Sprinklers are required in a portion of the building; sprinkler protection is not provided or the sprinkler system design is not adequate for the hazard protected in accordance with Section 903 of the NCBC. Category c—Sprinklers are not required; none are provided. Category d—Sprinklers are required in a portion of the building; sprinklers are provided in such portion; the system is one which complied with the code at the time of installation and is maintained and supervised in accordance with Section 903 of the NCBC. Category e—Sprinklers are required throughout; sprinklers are provided throughout in accordance with Chapter 9 of the NCBC. Category f—Sprinklers are not required throughout; sprinklers are provided throughout in accordance with Chapter 9 of the NCBC.
Note on D5: ◄Select the Type of Construction per Chapter 6 of the NCBC
Note on J5: ◄This Safety Parameter affects FS, ME, and GS
Note on P5: ◄This Safety Parameter affects FS, ME, and GS
Note on D6: ◄If the building is fully sprinklered select either NFPA 13 or NFPA 13R for type of system provided, for other types of systems or partial systems, or no system select "No".
Note on A8: The value for the building height and number of stories shall be the lesser value determined by the forumulas in 1401.6.1.1. Equation 14-1 Equation 14-2
Note on J8: ◄Category a—None. Category b—Existing smoke detectors in HVAC systems and maintained in accordance with the International Fire Code. Category c—Smoke detectors in HVAC systems. The detectors are installed in accordance with the requirements for new buildings in the International Mechanical Code. Category d—Smoke detectors throughout all floor areas other than individual sleeping units, tenant spaces and dwelling units. Category e—Smoke detectors installed throughout the floor area. Category f-Smoke detectors in corridors only.
Note on P8: ◄Category a—Standpipes are required; standpipe is not provided or the standpipe system design is not in compliance with Section 905.3 of the NCBC. Category b—Standpipes are not required; none are provided. Category c—Standpipes are required; standpipes are provided in accordance with Section 905 of the NCBC. Category d—Standpipes are not required; standpipes are provided in accordance with Section 905 of the NCBC.
Note on J9: ◄This Safety Parameter affects FS, ME, and GS
Note on P9: ◄This Safety Parameter affects FS, ME, and GS
Note on D11: ◄Insert the existing height of the building (feet)
Note on J12: ◄Category a—None. Category b—Fire alarm system with manual fire alarm boxes in accordance with Section 907.4 of the NCBC and alarm notification appliances in accordance with Section 907.5.2 of the NCBC. Category c—Fire alarm system in accordance with Section 907 of the NCBC. Category d—Category c plus a required emergency voice/alarm communications system and a fire command center that conforms to Section 911 of the NCBC and contains the emergency voice/alarm communications system controls, fire department communication system controls and any other controls specified in Section 911 of the NCBC where those systems are provided. Note: If there is no fire alarm system due to the fact that Section 907 of the NCBC is met, then select Category c rather than Category a for more accurate results.
Note on P12: ◄Answering "No" means there are no incidental use areas in the building or floor area being evaluated; Answering "Yes" means there are incidental accessory occupancies in accordance with Section 509 of the NCBC.
Note on D13: ◄Insert the number of stories in the existing building
Note on J13: ◄This Safety Parameter affects FS, ME, and GS
Note on P14: ◄Select the protection provided for the incidental accessory occupancy AS = Automatic Sprinkler System CRS = Construction capable of resisting the passage of smoke
Note on P15: ◄Select the required separation for the incidental use based on room or area per Table 509 of the NCBC.
Note on J16: ◄Category a—None. Category b—The building is equipped throughout with an automatic sprinkler system. Openings are provided in exterior walls at the rate of 20 square feet (1.86 m2) per 50 linear feet (15 240 mm) of exterior wall in each story and distributed around the building perimeter at intervals not exceeding 50 feet (15 240 mm). Such openings shall be readily openable from the inside without a key or separate tool and shall be provided with ready access thereto. In lieu of operable openings, clearly and permanently marked tempered glass panels shall be used. Category c—One enclosed exit stairway, with ready access thereto, from each occupied floor of the building. The stairway has operable exterior windows and the building has openings in accordance with Category b. Category d—One smokeproof enclosure and the building has openings in accordance with Category b. Category e—The building is equipped throughout with an automatic sprinkler system. Each floor area is provided with a mechanical air-handling system designed to accomplish smoke containment. Return and exhaust air shall be moved directly to the outside without recirculation to other floor areas of the building under fire conditions. The system shall exhaust not less than six air changes per hour from the floor area. Supply air by mechanical means to the floor area is not required. Containment of smoke shall be considered as confining smoke to the fire area involved without migration to other floor areas. Any other tested and approved design which will adequately accomplish smoke containment is permitted. Category f—Each stairway shall be one of the following: a smokeproof enclosure in accordance with Section 1023.11 of the NCBC; pressurized in accordance with Section 909.20.5 of the NCBC or shall have operable exterior windows. Footnote a: The valuse for B, M, R, F, and S occupancies that do not meet catagory d or e for Section 1401.6.8 shall be 0.
Note on J17: ◄This Safety Parameter affects ME and GS
Note on P17: ◄This Safety Parameter affects FS, ME, and GS
Note on D18: ◄This Safety Parameter affects FS, ME, and GS
Note on J20: ◄Category a—Compliance with the minimum required means of egress capacity or number of exits is achieved through the use of a fire escape in accordance with Section 405. Category b—Capacity of the means of egress complies with Section 1004 of the NCBC and the number of exits complies with the minimum number required by Section 1021 of the NCBC. Category c—Capacity of the means of egress is equal to or exceeds 125 percent of the required means of egress capacity, the means of egress complies with the minimum required width dimensions specified in the code and the number of exits complies with the minimum number required by Section 1021 of the NCBC. Category d—The number of exits provided exceeds the number of exits required by Section 1021 of the NCBC. Exits shall be located a distance apart from each other equal to not less than that specified in Section 1015.2 of the NCBC. Category e—The area being evaluated meets both Categories c and d.
Note on P20: ◄Category a - Smoke compartment size is equal to or less than 22,500 sq. ft. Category b - Smoke compartment size is greater than 22,500 sq. ft. Category c - Smoke compartments are not provided.
Note on D21: ◄Insert the perimeter Perimeter in (feet) of the entire existing building
Note on J21: ◄This Safety Parameter affects ME and GS
Note on P21: ◄This Safety Parameter affects FS, ME, and GS
Note on D22: ◄Insert the perimeter (feet) of the existing building that fronts a public way greater than or equal to 20 ft in width in accordanc with 506.3.2 of the NCBC
Note on D23: ◄Insert the width of the public way (feet). W per Equation 5-4 of the NCBC
Note on J24: ◄Insert distance (feet) of the longest dead end path
Note on D25: ◄Insert the actual building area (ft2)
Note on J25: ◄Insert the width of the largest dead end (feet) (considered no dead end when the length to width ratio is less than 2.5:1)
Note on P25: ◄Category a - (mobile) Pateints are capable of self-preservation without assistance. Category b - (not mobile) Patients rely on assistance for evacuation or relocation. Category c - (not movable) Patients cannot be evacuated or relocated.
Note on J26: ◄This Safety Parameter affects ME and GS
Note on P26: ◄This Safety Parameter affects ME and GS
Note on P28: Category a - Smoke compartment has 1 to 10 patients Category b - Smoke compartment has more than 10 to 40 patients Category c - Smoke compartment has greater than 40 patients
Note on J29: ◄Insert the maximum actual travel distance to an approved exit (feet)
Note on P29: ◄This Safety Parameter affects ME and GS
Note on D31: ◄This Safety Parameter affects FS, ME, and GS
Note on J31: ◄Maximum allowable travel distance per T1017.2. Error indications not allowed for single exit.
Note on P31: Category a - Attendant-to-patient concentration is 1:5. Category b - Attendant-to-patient concentration is 1:6 to 1:10. Category c - Attendant-to-patient concentration is greater than 1:10 or no patients.
Note on J32: ◄This Safety Parameter affects ME and GS
Note on P32: ◄This Safety Parameter affects ME and GS
Note on D34: ◄Insert the net area of the compartment size (ft2) Note: Fire barriers and Horizontal assemblies of 2 hours in accordance with Sections 707 and 711 of the NCBC create comparments. Where the building is not divided into more than one compartment, the compartment size shall be taken as the total floor area on all floors.
Note on J35: ◄Category a—No elevator. Category b—Any elevator without Phase I emergency recall operation and Phase II emergency in-car operation. Category c—All elevators with Phase I emergency recall operation and Phase II emergency in-car operation as required by the International Fire Code. Category d—All meet Category c; or Category b where permitted to be without Phase I emergency recall operation and Phase II emergeancy in-car operation; and at least one elevator that complies with new construction requirements serves all occupied floors.
Note on J36: ◄Answering "Yes" means there is less than 25 feet of travel above or below the primary level of elevator access for emergency fire fighting or rescue personnel;
Note on D37: ◄This Safety Parameter affects FS, ME, and GS
Note on D40: ◄Category a—No fire partitions; incomplete fire partitions; no doors; doors not self-closing or automatic-closing. Category b—Fire partitions or floor assemblies with less than a 1-hour fire-resistance rating or not constructed in accordance with Sections 708 or 711 of the NCBC, respectively. Category c—Fire partitions with a 1-hour or greater fire-resistance rating constructed in accordance with Section 708 of the NCBC and floor assemblies with a 1-hour but less than 2-hour fire-resistance rating constructed in accordance with Section 711 of the NCBC, or with only one tenant within the floor area. Category d—Fire barriers with a 1-hour but less than 2-hour fire-resistance rating constructed in accordance with Section 707 of the NCBC and floor assemblies with a 2-hour or greater fire-resistance rating constructed in accordance with Section 711 of the NCBC. Category e—Fire barriers and floor assemblies with a 2-hour or greater fire-resistance rating and constructed in accordance with Sections 707 and 711 of the NCBC, respectively.
Note on J40: ◄This Safety Parameter affects FS, ME, and GS
Note on D41: ◄This Safety Parameter affects FS, ME, and GS
Note on J43: ◄Category a—Means of egress lighting and exit signs not provided with emergency power in accordance with Section 2702 of the NCBC. Category b—Means of egress lighting and exit signs provided with emergency power in accordance with Section 2702 of the NCBC. Category c—Emergency power provided to means of egress lighting and exit signs, which provides protection in the event of power failure to the site or building.
Note on D44: ◄Category a—No fire partitions; incomplete fire partitions; no doors; or doors not self-closing. Category b—Less than 1-hour fire-resistance rating or not constructed in accordance with Section 708.4 of the NCBC. Category c—1-hour to less than 2-hour fire-resistance rating, with doors conforming to Section 716 of the NCBC or without corridors as permitted by Section 1020 of the NCBC. Rated corridor not required per the NCBC Category d—2-hour or greater fire-resistance rating, with doors conforming to Section 716 of the NCBC. Note: Corridors not providing at least one-half the exit access travel distance for all occupants on a floor shall use Category b.
Note on J44: ◄Answering "Yes" means there are two or more exits; Answering "No" means there is a minimum of one exit
Note on D45: ◄This Safety Parameter affects FS, ME, and GS
Note on J45: ◄This Safety Parameter affects ME and GS
Note on D48: ◄Insert the maximum number of floors connected; if the structure is a one story building (EBS=1) then insert 1 for this value.
Note on J48: ◄Category a—Occupancies separated by minimum 1-hour fire barriers or minimum 1-hour horizontal assemblies, or both. Category b—Separations between occupancies in accordance with Section 508.4 of the NCBC. Category c—Separations between occupancies having a fire-resistance rating of not less than twice that required by Section 508.4 of the NCBC.
Note on D49: ◄Select the vertical opening protection based on Table 1401.6.6(1)
Note on J49: ◄Answer "Yes" if the building has two or more occupancies that are not the same occupancy classification.
Note on J51: ◄Answering "Yes" means the mixed occupancies are separated by one of the qualifying categories. Answering "No" requries a separate evaluation for each occupancy and the lower score for each occupancy for each section shall apply to the entire building.
Note on D53: ◄This Safety Parameter affects FS, ME, and GS
Note on J53: ◄This Safety Parameter affects FS and GS

## Detailed Analysis
[10 empty] | Yes/No | Construction Type | Occupancy Classification | Incidental Use per T509 of the NCBC |  | Allowable Height Above Grade Plane Calculation
Chapter 14 Evaluation - Detailed Analysis | [14 empty] | Occupancy Group |  | R
[17 empty] | 1A | 1B | 2A | 2B | 3A | 3B | 4 | 5A | 5B
1401.6.1 - Building Height | [14 empty] | Table 503 |  | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40
[15 empty] | Stories | A1 | UL | 5 | 3 | 2 | 3 | 2 | 3 | 2 | 1
Occupancy | R1 |  | Height Value, feet (Eq. 14-1) |  |  | 3.68 | [9 empty] | A2 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1
Construction Type | IIA |  | Height Value, stories (Eq. 14-2) |  |  | 4 |  |  |  | No | IA | A1 | 2 Hrs & AS |  |  | A3 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1
Sprinklers? | NFPA 13 | [8 empty] | Yes | IB | A2 | 2 Hrs, or 1 Hr & AS |  |  | A4 | UL | 11 | 3 | 2 | 3 | 2 | 3 | 2 | 1
AH, feet | 65 | [9 empty] | IIA | A3 | 1 Hr & AS |  |  | A5 | UL | UL | UL | UL | UL | UL | UL | UL | UL
AH Increase | 85 | [8 empty] | Sprinkler Protection | IIB | A4 | 1 Hour |  |  | B | UL | 11 | 5 | 3 | 5 | 3 | 5 | 3 | 2
AS, stories | 4 | [9 empty] | IIIA | B | 1 Hr, or AS w/ CRS |  |  | E | UL | 5 | 3 | 2 | 3 | 2 | 3 | 1 | 1
AS Increase | 5 | [9 empty] | IIIB | E | AS w/ CRS |  |  | F1 | UL | 11 | 4 | 2 | 3 | 2 | 4 | 2 | 1
EBH, feet | 39 | [9 empty] | IV | F1 | 1 Hr or AS |  |  | F2 | UL | 11 | 5 | 3 | 4 | 3 | 5 | 3 | 2
EBS, stories | 1 | [9 empty] | VA | F2 |  |  |  | I2 | UL | 4 | 2 | 1 | 1 | NP | 1 | 1 | NP
CF | 1 | [9 empty] | VB | I2 | Incidental Use Protection Provided 1401.6.19 |  |  | M | UL | 11 | 4 | 2 | 4 | 2 | 4 | 3 | 1
Safety Parameter | [7 empty] | 3.68 |  | No |  | M |  |  |  | R1 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2
[10 empty] | NFPA 13 |  | R1 |  |  |  | R2 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2
1401.6.2 - Building Area | [9 empty] | NFPA 13R |  | R2 |  |  |  | R3 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 3
[12 empty] | R3 |  |  |  | R4 | UL | 11 | 4 | 4 | 4 | 4 | 4 | 3 | 2
P, feet | 3600 |  | Area Value (Eq. 14-4) |  | 63.4 |  |  |  |  | Categories | Fire Resistance Rating | R4 |  |  |  | S1 | UL | 11 | 4 | 2 | 3 | 2 | 4 | 3 | 1
F, feet | 1500 | [10 empty] | S1 | None |  |  | S2 | UL | 11 | 5 | 3 | 4 | 3 | 5 | 4 | 2
W, feet | 30 | [10 empty] | S2 | 1 Hour |  |  | U | UL | 5 | 4 | 2 | 3 | 2 | 4 | 2 | 1
If (Eq. 5-2) | 0.17 | [11 empty] | AS
Is | 3 | [10 empty] | NO IDEA | AS w/ CRS |  | Table 503 |  |  | Row Value |  | 4
At, per story | 24000 | [11 empty] | 1 Hr & AS |  | Area
Aa per story | 100080 | [8 empty] | Category a | None |  | 2 Hours |  |  |  | 1A | 1B | 2A | 2B | 3A | 3B | 4 | 5A | 5B
Aa building | 100080 | [8 empty] | Category b | < 1 hr |  | 2 Hrs & AS |  |  |  | UL | UL | 65 | 55 | 65 | 55 | 65 | 50 | 40
Aactual per story | 24000 | [8 empty] | Category c | 1hr - 2hr |  |  |  |  | A1 | UL | UL | 15500 | 8500 | 14000 | 8500 | 15000 | 11500 | 5500
Safety Parameter | [7 empty] | 10.5 |  | Category d | > 2 hr |  |  |  |  | A2 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000
[10 empty] | Category e |  | 1st/Basement |  |  |  | A3 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000
1401.6.3 - Compartmentation | [9 empty] | Category f |  | 2nd |  |  |  | A4 | UL | UL | 15500 | 9500 | 14000 | 9500 | 15000 | 11500 | 6000
[12 empty] | 3rd |  |  |  | A5 | UL | UL | UL | UL | UL | UL | UL | UL | UL
Occupancy |  | Categories | [13 empty] | B | UL | UL | 37500 | 23000 | 28500 | 19000 | 36000 | 18000 | 9000
|  | a | b | c | d | e | [9 empty] | E | UL | UL | 26500 | 14500 | 23500 | 14500 | 25500 | 18500 | 9500
A1, A3 | N | 0 | 6 | 10 | 14 | 18 | [9 empty] | F1 | UL | UL | 25000 | 15500 | 19000 | 12000 | 33500 | 14000 | 8500
A2 | N | 0 | 4 | 10 | 14 | 18 |  |  |  | Allowable Story 5-2 |  | Sprinkler or Non-sprinkler (max3) |  |  |  | F2 | UL | UL | 37500 | 23000 | 28500 | 18000 | 50500 | 21000 | 13000
A4, B, E, S2 | N | 0 | 5 | 10 | 15 | 20 |  |  |  | 104160 |  | 4 |  | 5 |  | I2 | UL | UL | 15000 | 11000 | 12000 | NP | 12000 | 9500 | NP
F, M, R, S1 | Y | 0 | 4 | 10 | 16 | 22 | [9 empty] | M | UL | UL | 21500 | 12500 | 18500 | 12500 | 20500 | 14000 | 9000
[16 empty] | R1 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000
Compartment Size |  | 10001 | [7 empty] | Interp. | [5 empty] | R2 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000
Category |  | a | 2 | [6 empty] | #VALUE! | [5 empty] | R3 | UL | UL | UL | UL | UL | UL | UL | UL | UL
Compartmentation Value |  | 0 | [13 empty] | R4 | UL | UL | 24000 | 16000 | 24000 | 16000 | 20500 | 12000 | 7000
[16 empty] | S1 | UL | 48000 | 26000 | 17500 | 26000 | 17500 | 25500 | 14000 | 9000
Safety Parameter | [7 empty] | 0 | [7 empty] | S2 | UL | 79000 | 39000 | 26000 | 39000 | 26000 | 38500 | 21000 | 13500
[16 empty] | U | UL | 35500 | 19000 | 8500 | 14000 | 8500 | 18000 | 9000 | 5500
1401.6.4 - Tenant and Dwelling Unit Separation
Occupancy |  | Categories
|  | a | b | c | d | e
A1 | N | 0 | 0 | 0 | 0 | 1
A2 | N | -5 | -3 | 0 | 1 | 3
A3, A4, B, E, F, M, S1 | N | -4 | -3 | 0 | 2 | 4 | [9 empty] | Allowable Height |  |  |  | Row Values |  |  | Allowable Stories 13R
R | Y | -4 | -2 | 0 | 2 | 4 | [9 empty] | IA | UL |  |  | IA | 2 |  |  | IA | IB | IIA | IIB | IIIA | IIIB | IV | VA | VB
I2 | N | 0 | 1 | 2 | 3 | 4 | [9 empty] | IB | 160 |  |  | IB | 3 |  | R1 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3
S2 | N | -5 | -2 | 0 | 2 | 4 | [9 empty] | IIA | 65 |  |  | IIA | 4 |  | R2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3
[16 empty] | IIB | 55 |  |  | IIB | 5 |  | R3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Separation Category: |  | c | 4 | [12 empty] | IIIA | 65 |  |  | IIIA | 6 |  | R4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3
[16 empty] | IIIB | 55 |  |  | IIIB | 7
Safety Parameter | [7 empty] | 0 | [7 empty] | IV | 65 |  |  | IV | 8
[16 empty] | VA | 50 |  |  | VA | 9
1401.6.5 - Corridor Walls | [15 empty] | VB | 40 |  |  | VB | 10
Occupancy |  | Categories
|  | a | b | c | d
A1 | N | -10 | -4 | 0 | 2 | [10 empty] | Table 1401.6.6(2) - Construction Type Factor
A2 | N | -30 | -12 | 0 | 2 | [10 empty] | IA | 1.2
A3, F, M, R, S1 | Y | -7 | -3 | 0 | 2 | [10 empty] | IB | 1.5
A4, B, E, S2 | N | -5 | -2 | 0 | 5 | [10 empty] | IIA | 2.2
I2 | N | -10 | 0 | 1 | 2 | [10 empty] | IIB | 3.5
[16 empty] | IIIA | 2.5
Corridor Walls Category: |  | c | 4 | [12 empty] | IIIB | 3.5
[16 empty] | IV | 2.3
Safety Parameter | [7 empty] | 0 | [7 empty] | VA | 3.3
[16 empty] | VB | 7
1401.6.6 - Vertical Openings
Number of Floors Connected: |  | 1
Protection |  | Value
None | Y | -2
Less than 1 hour | N | -1
1 to less than 2 hours | N | 1
2 hours or more | N | 2
Construction Type Factor (CF): |  | 2.2
Protection Value (PV): |  | N/A
Vertical Opening Value (VO): |  | N/A
Safety Parameter | [7 empty] | 2
1401.6.7 - HVAC Systems
HVAC System Category: |  | b
Safety Parameter | [7 empty] | -5
1401.6.8 - Automatic Fire Detection
Occupancy |  | Categories
|  | a | b | c | d | e | f
A1, A3, F, M, R, S1 | Y | -10 | -5 | 0 | 2 | 6 | 0
A2 | N | -25 | -5 | 0 | 5 | 9 | 0
A4, B, E, S2 | N | -4 | -2 | 0 | 4 | 8 | 0
I2 | N | NP | NP | NP | 4 | 5 | 2
Fire Detection Category: |  | b | 3
Safety Parameter | [7 empty] | -5
1401.6.9 - Fire Alarm Systems
Occupancy |  | Categories
|  | a | b | c | d
A1, A2, A3, A4, B, E, R | Y | -10 | -5 | 0 | 5
F, M, S | N | 0 | 5 | 10 | 15
I2 | N | -4 | 1 | 2 | 5
Fire Alarm Category: |  | b | 3
Safety Parameter | [7 empty] | -5
1401.6.10 - Smoke Control
Occupancy |  | Categories
|  | a | b | c | d | e | f
A1, A2, A3 | N | 0 | 1 | 2 | 3 | 6 | 6
A4, E | N | 0 | 0 | 0 | 1 | 3 | 5
B, M, R | Y | 0 | 2 | 3 | 3 | 3 | 4
F, S | N | 0 | 2 | 2 | 3 | 3 | 3
I2 | N | -4 | 0 | 0 | 0 | 3 | 0
Smoke Control Category: |  | a | 2
Compliance with Category d or e of 1401.6.8.1? |  |  | No
Safety Parameter | [7 empty] | 0
1401.6.11 - Means of Egress Capacity
Occupancy |  | Categories
|  | a | b | c | d | e
A1, A2, A3, A4, E | N | -10 | 0 | 2 | 8 | 10
B, F, S | N | -1 | 0 | 0 | 0 | 0
M | N | -3 | 0 | 1 | 2 | 4
R | Y | -3 | 0 | 0 | 0 | 0
Means of Egress Category: |  | c | 4
Safety Parameter | [7 empty] | 0
1401.6.12 - Dead Ends
Category a | 70
Category b | 20
Dead End Category | a
Dead End Length | 70
Dead End Width | 5
Largest Dead End L/W | 14
Safety Parameter | [7 empty] | -2
1401.6.13 - Exit Access Travel Distance
[13 empty] | 13/no | 13R
Maximum Actual Travel Distance: |  |  | 270 | [9 empty] | 250 | Not 13R
Maximum Allowable Travel Distance: |  |  | 250 |  |  |  | 75 |  | Error |  |  |  | 250
Safety Parameter | [7 empty] | -1.6
1401.6.14 - Elevator Control
Elevator Travel |  | Categories
|  | a | b | c | d
Less than 25 feet of travel above or below the primary level of elevator access | N | -2 | 0 | 0 | 2
Travel of 25 feet or more above or below the primary level of elevator access | Y | -4 | NP | 0 | 4
Elevator Control Category: |  | c | 4
Safety Parameter | [7 empty] | 0
1401.6.15 - Means of Egress Emergency Lighting
Number of Exits |  | Categories
|  | a | b | c
Two or more exits | Y | NP | 0 | 4
Minimum of one exit | N | 0 | 1 | 1
Emergency Lighting Category: |  | c | 4
Safety Parameter | [7 empty] | 4
1401.6.16 - Mixed Occupancies
Occupancy |  | Categories
|  | a | b | c
A1, A2, R | Y | -10 | 0 | 10
A3, A4, B, E, F, M, S | N | -5 | 0 | 5
I2 | N | NP | 0 | 5
Mixed Occupancy Category |  | a | 2
Are there mixed occupancies? |  | Y
Separation between mixed occupancies? |  | Y
Safety Parameter | [7 empty] | -10
1401.6.17 - Automatic Sprinklers
Occupancy |  | Categories
|  | a | b | c | d | e | f
A1, A3, F, M, R, S1 | Y | -6 | -3 | 0 | 2 | 4 | 6
A2 | N | -4 | -2 | 0 | 1 | 2 | 4
A4, B, E, S2 | N | -12 | -6 | 0 | 3 | 6 | 12
I2 | N | NP | NP | NP | 8 | 10 | NP
Automatic Sprinklers Category |  | c | 4
Safety Parameter | [7 empty] | 0
1401.6.18 - Standpipes
Occupancy |  | Categories
|  | a | b | c | d
A1, A3, F, M ,R , S1 | Y | -6 | 0 | 4 | 6
A2 | N | -4 | 0 | 2 | 4
A4, B, E, S2 | N | -12 | 0 | 6 | 12
I2 | N | -2 | 0 | 1 | 2
Standpipe Category: |  | a | 2
Safety Parameter | [7 empty] | -6
1401.6.19 - Incidental Accessory Occupancy
Protection Required by Table 509.4.2 of the NCBC |  | Protection Provided
|  | None | 1 Hour | AS | AS with CRS | 1 Hour and AS | 2 Hours | 2 Hours and AS
|  | Y | N | N | N | N | N | N
2 Hours and AS | N | -4 | -3 | -2 | -2 | -1 | -2 | 0
2 Hours, or 1 Hour and AS | N | -3 | -2 | -1 | -1 | 0 | 0 | 0
1 Hour and AS | N | -3 | -2 | -1 | -1 | 0 | -1 | 0
1 Hour | Y | -1 | 0 | -1 | 0 | 0 | 0 | 0
1 Hour, or AS with CRS | N | -1 | 0 | -1 | 0 | 0 | 0 | 0
AS with CRS | N | -1 | -1 | -1 | 0 | 0 | -1 | 0
1 Hour or AS | N | -1 | 0 | 0 | 0 | 0 | 0 | 0
Specific Occupancy Areas? |  | Yes
Type of Protection Provided: |  | None |  | 2
Safety Parameter | [7 empty] | -1
1401.6.20 - Smoke Compartmentation
Occupancy |  | Categories
|  | a | b | c
A,B,E,F,M,R,S | Y | 0 | 0 | 0
I2 | N | 0 | NP | NP
Smoke Compartmentation Category: |  | b | 3
Safety Parameter | [7 empty] | 0
1401.6.21 - I-2 Smoke Compartment Safety
1401.6.21.1 - Patient Ability for Self Preservation
Occupancy |  | Categories
|  | a | b | c
I2 | N | 1 | 2 | 3
Self Preservation Catgeory: | a | 2
Safety Parameter | [7 empty] | 0
1401.6.21.2 - Patient Concentration
Occupancy |  | Categories
|  | a | b | c
I2 | N | 1 | 2 | 3
Patient Concentration Category: |  | b | 3
Safety Parameter | [7 empty] | 0
1401.6.21.3 - Attendant to Patient Ratio
Occupancy |  | Categories
|  | a | b | c
I2 | N | 1 | 2 | 3
Attendant to Patient Ratio Category: |  | a | 2
Safety Parameter | [7 empty] | 0
Table 1401.7 - Summary Sheet - Building Code
|  |  | Fire Safety (FS) |  | Means of Egress (ME) |  | General Safety (GS)
1401.6.1 Building Height |  |  | 3.68 |  | 3.68 |  | 3.68
1401.6.2 Building Area |  |  | 10.5 |  | 10.5 |  | 10.5
1401.6.3 Compartmentation |  |  | 0 |  | 0 |  | 0
1401.6.4 Tenant & Dwelling Unit Separation |  |  | 0 |  | 0 |  | 0
1401.6.5 Corridor Walls |  |  | 0 |  | 0 |  | 0
1401.6.6 Vertical Openings |  |  | 2 |  | 2 |  | 2
1401.6.7 HVAC Systems |  |  | -5 |  | -5 |  | -5
1401.6.8 Automatic Fire Detection |  |  | -5 |  | -5 |  | -5
1401.6.9 Fire Alarm Systems |  |  | -5 |  | -5 |  | -5
1401.6.10 Smoke Control |  |  | --- |  | 0 |  | 0
1401.6.11 Means of Egress Capacity |  |  | --- |  | 0 |  | 0
1401.6.12 Dead Ends |  |  | --- |  | -2 |  | -2
1401.6.13 Maximum Exit Access Travel Distance |  |  | --- |  | -1.6 |  | -1.6
1401.6.14 Elevator Control |  |  | 0 |  | 0 |  | 0
1401.6.15 Means of Egress Emergency Lighting |  |  | --- |  | 4 |  | 4
1401.6.16 Mixed Occupancies |  |  | -10 |  | ---- |  | -10
1401.6.17 Automatic Sprinklers |  |  | 0 |  | 0 |  | 0
1401.6.18 Standpipes |  |  | -6 |  | -6 |  | -6
1401.6.19 Incidental Accessory Occupancy |  |  | -1 |  | -1 |  | -1
1401.6.20 Smoke Compartmentation |  |  | 0 |  | 0 |  | 0
1401.6.21.1 Patient Ability for Self Preservation |  |  | --- |  | 0 |  | 0
1401.6.21.2 Patient Concentration |  |  | --- |  | 0 |  | 0
1401.6.21.3 Attendent-to-Patient Ratio |  |  | --- |  | 0 |  | 0
Building Score - Total Value |  |  | -15.82 |  | -5.42 |  | -15.42
Table 1401.8 Mandatory Safety Scores
Occupancy |  | Fire Safety (MFS) |  | Means of Egress (MME) |  | General Safety (MGS)
A1 | N | 20 |  | 31 |  | 31
A2 | N | 21 |  | 32 |  | 32
A3 | N | 22 |  | 33 |  | 33
A4, E | N | 29 |  | 40 |  | 40
B | N | 30 |  | 40 |  | 40
F | N | 24 |  | 34 |  | 34
I2 | N | 19 |  | 34 |  | 34
M | N | 23 |  | 40 |  | 40
R | Y | 21 |  | 38 |  | 38
S1 | N | 19 |  | 29 |  | 29
S2 | N | 29 |  | 39 |  | 39
|  | MFS = | 21 | MME = | 38 | MGS = | 38
Evaluation
| Building Score |  | Mandatory Score |  | Pass/Fail?
Fire Safety | -15.82 |  | 21 |  | FAIL
Means of Egress | -5.42 |  | 38 |  | FAIL
General Safety | -15.42 |  | 38 |  | FAIL