Hydrant Inspection/Testing

Data Requirements

- Hydrant identification number

- Hydrant location, use street names, numbers and intersections as needed

- Which service level/pressure zone serves the hydrant

- Number and size of outlets on hydrant

Inspection/testing Requirements

- Remove caps , check treads for damage and ease of operation

- Lubricate, as needed, per manufacturers recommendations

- With on or more caps removed from hydrant, open valve stem and free flow hydrant, check for any obvious restrictions or contaminants, close valve stem

- Open valve stem fully, pressurize hydrant.

- Check valve stem ease of operation, check hydrant for any water leaks while under pressure

- Close valve stem fully, remove pressure gauge, check for adequate barrel drainage or check for a vacuum with a gauge if possible

- Provide for an obstructed and obvious view of hydrant from roadway (cut grass, remove debris, etc. as needed)

- Paint per local protocols/requirements, as needed

# HYDRANT RECORD CARD

| LOCATION |  | NUMBER |  | WATER AVAILABLE |  | GPM AT 20 PSI |  | MAIN SIZE |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TYPE SIZE LATERAL 2-WAY ______________ 3-WAY _______________ LATERAL GATES YES ________ NO ________ |  |  |  |  |  |  |  |  |  |
| HEIGHT FROM GROUND 2 ½” OUTLETS |  |  |  |  |  |  |  |  |  |
| INSPECTED |  |  |  |  |  | PRESSURES |  |  |  |
| DATE | TIME | BY WHOM | CONDITION | OUT OF SERVICE | IN SERVICE | STATIC | RESI. | FLOWING | REMARKS |

# HYDRANT INSPECTION

Frequency:

Inspections include pressure tested, flushed, caps lubricated, etc. Department must document the inspection Department will provide 3 most recent years of hydrant inspection records

Frequency of Inspection	Points

1 year				   30

2 years				   20

3 years				   10

4 years				     5

5 years or more		           No Credit

Condition:

- Standard condition (no leaks, open easily, good ground clearance, not damaged in any way, conspicuous and well located for use by a Engine)

# HYDRANT FLOW TESTING INSPECTION

Frequency of Flow Testing	        Points 	Points w/Marking Program

5 year		       			   40			   50

6 years		       			   30			   37.5

7 years		   			   20			   25

8 years		    			   10			  12.5

9 years		     			     5			   6.25

10 years or more           	    No Credit	          No Credit

To obtain credit for Fire Flow Testing a 2 hydrant test must be conducted.

Flow Hydrant

Static and Residual Hydrant