## Sheet1
Building Foot Print |  | Length = |  | Width = |  | Sq. Ft. = | 0
[5 empty] | Total Sq. Ft. = |  | 0
*Add height for
each floor | Ceiling Height = |  |  |  |  | Cu. Ft. = | 0
*Note: take 1/2 of
pitched roof height | Attic Height = |  |  |  |  | Cu. Ft. = | 0
Additional space: | [5 empty] | Cu. Ft. = | 0
(porch, etc.) | Length |  | Width |  | Height
[5 empty] | Total Cu. Ft. = |  | 0
| Total Cu. Ft. = |  | 0 | OHC = | 7 | Gallons = | 0
*Note* Occupancy Hazard Classification number is 7 for dwellings, small office
complexes and similar constructed facilities. Refer to NFPA 1142 for
other types of structures.
| Gallons = |  | 0 | CCN = | 1 | Gallons = | 0
*Note* Type II Construction .75. Ex: Cinderblock, approved non-combustible material.
Type III Construction 1.0. Ex: Brick vaneer, approved non-combustible material etc.
Type V Construction 1.5. **Dwellings max 1.0 CCN per NFPA 1142**
| Gallons = |  | 0 | Exp = | 1 | Gallons = | 0
*Note* Any structure within 50' of burn structure is considered an exposure and
requires total gallons to be multiplied by 1.5. DO NOT add .5 for each additional exposures.
| Total Gallons Required |  |  |  | GPM
| Up to 15,000 Gallons |  |  |  | 250 GPM
| 15,001 to 22,500 Gallons |  |  |  | 500 GPM
| 22,501 to 30,000 Gallons |  |  |  | 750 GPM
| 30,000 or more |  |  |  | 1000 GPM
|  |  | Total GPM for NFPA 1142 |  |  |  | 250
**In accordance with NFPA 1403, an additional water supply in the amount of 50% of total required
fire flow must be available to handle unforseen situations.**
| Gallons = | 0 | at | 250 | GPM | for about | 0
Minutes
| 0 | Gallons | x 1.5 = | 0
NFPA 1403
requirement

## Sheet2 (hidden)
3 | 0.5 | 0 | 0
4 | 0.75 | 1 | 1
5 | 1 | 2 | 2
6 | 1.5 | 3 | 3
7 |  | 4 | 4
5
6
7